## Revised OPEX Estimate
| SITE | Labour | Chemicals | Tanker | Original OPEX Estimates | Labour | Chemicals | Tanker | Revised OPEX Estimates | 2019 |  | 2020 |  |  | Mature Compliance Risk (2018 Assessment) RAG Status | Mature Compliance Risk (2020 Assessment) RAG Status | Site Projected to Fail | Mature Compliance Assessment Comments 2020 | Possible Mature Compliance Base Maintenance Intervention | PC21 Delivery Project
[10 empty] | Audit Sample Results Exceedance/No of Samples | Unannounced Sample Results Exceedance/No of samples BOD/SS/A | Audit Sample Results Exceedance/No of samples | Unannounced Sample Results Exceedance/No of samples BOD/SS/A | Onsite Spot Sample Results Exceedance/No of samples (BOD/Clarity)/(Turbidity/SS)/A
1 | Aghalee | 2433.6 | 0 | 0 | 2433.6 | 15539.48 | 1622.4 | 0 | 17161.88 | 1/12 1/0/- | N/A | 0/8 | 0/4 | 0/2 | AMBER | AMBER |  | Revised OPEX estimate should provide best endeavours to reduce risk of failing under an unannounced schedule, though no guarantee can be given. Risk remains wth flow compliance. Although increased deep cleans should allow the works to maintain the current maximum levels that can be achieved, an upgrade with hi-flow MBR panels may be required. | Replacement of MBR panels with high flow membranes | No
1 | Aghanloo | 3245.84 | 0 | 16000 | 19245.84 | 4421.08 | 0 | 16000 | 20421.08 | 0/12 | 1/17 0/1/- | 0/6 | 0/2 | 0/1 | RED (High) | RED (SEVERE) | Yes | It is felt the revised OPEX estimate should provide best endeavours to reduce risk of failing under an unannounced schedule, though no guarantee can be given. TE remains a concern which may have a bearing on future compliance. This is also an aged asset. | Improved inlet flow control (FFT and storm) and base maintenance on filter bed. Assets are old in poor condition. | Yes
1 | Annahilt | 1622.4 | 0 | 0 | 1622.4 | 11457.44 | 0 | 0 | 11457.44 | 0/6 | N/A | 0/3 | 0/3 | 0/1 | GREEN | GREEN |  | No significant operational risk associated with this site. Revised OPEX estimate should provide best endeavours to reduce risk of failing under an unannounced schedule, though no guarantee can be given. | No additional Mature Compliance Base Maintenance required | No | 1
1 | Annsborough | 9734.4 | 0 | 0 | 9734.4 | 12759.52 | 0 | 0 | 12759.52 | 0/12 | 5/47 1/1/3 | 1/15 | 0/1 | 0/8 | AMBER | RED (HIGH) |  | The ineffectiveness of the management of flows has been identified as a compliance risk. A combination of storm removal from the network and the provision of a more effective and efficient inlet works to manage flows and either primary settlement or balanceing tank. Without this capital intervention Annsborough would remain at risk. | A combination of storm removal from the network and the provision of a more effective and efficient inlet works to manage flows and either primary settlement or balanceing tank. | Yes
1 | Ardglass | 13384.4 | 3500 | 36400 | 53284.4 | 11293.58 | 1540 | 12050.5 | 24884.08 | 0/12 | 5/40 2/3/- | 0/8 | 0/2 | 0/1 | RED (High) | RED (HIGH) |  | Outside of fishing season process performs satisfactorily with no significant problems or concerns. Revised OPEX estimates is to operate and manage process during increased fish factory output. During high factory production process is at high risk of failing. More effective policing/management of TE would significantly reduce risk. | Sludge management of site possibly too small. Sludge storage and sludge thickening plant. No matter what base maintenance is carried out unless TE is managed the site will be at risk. | Yes
1 | Armoy | 2433.6 | 0 | 0 | 2433.6 | 4991.33 | 0 | 8000 | 12991.33 | 0/12 | 2/36 0/1/1 | 0/6 | 0/1 | N/A | RED (High) | RED (HIGH) |  | It is felt the revised OPEX estimate should reduce risk of failing under an unannounced schedule, though no guarantee can be given. | Inlet flow control. Storm removal from the network. Provide Sludge storage facilities. Observation - Assets are also old. | No
1 | Banbridge | 11356.8 | 0 | 0 | 11356.8 | 6552.52 | 0 | 0 | 6552.52 | 0/12 | 0/48 | 0/6 | 0/2 | 0/2 | AMBER | GREEN |  | As site is a manned site with week-end planned overtime undertaken, increased OPEX would provide limited improvement. It is felt the revised OPEX estimate (especially around increased planned week-end work) should reduce risk of failing under an unannounced schedule, though no guarantee can be given. | No additional Mature Compliance Base Maintenance required | No | 1
1 | Belfast | 16224 | 0 | 0 | 16224 | 7865.52 | 0 | 0 | 7865.52 | 0/49 (10no TN exceedances) | N/A | 0/27 (2no TN exceedances) | 1/4 0/1/0 | 0/9 | RED (High) | RED (HIGH) |  | With Belfast being a manned site 7 days/week, the opportunity to increase OPEX to reduce risk of failing is limited. In its current stage will remain at risk, especially for TN. With the continued permitting of development, the risk of failing will only increase. Capital intervention is required to address risk. | No additional Mature Compliance Base Maintenance required. Belfast Phase 0 addressing elements of routine base maintenance needs. | Yes | 1
1 | Bellaghy | 4867.2 | 0 | 18400 | 23267.2 | 4542.32 | 0 | 18400 | 22942.32 | 0/6 | 13/22 4/8/1 | 0/7 | 1/1 1/0/0 | 1/1 1/0/0 | RED (High) | RED (SEVERE) | Yes | Process was trial which has been retained. Process very temperamental and difficult to operate. Will remain a risk in its current form. | Risk will be addressed by PC21 Capital Delivery Project. No Mature Compliance base maintenance solution available | Yes | 1
1 | Castlederg | 6489.6 | 0 | 0 | 6489.6 | 10516.86 | 0 | 0 | 10516.86 | 0/6 | 5/24 1/3(2 U/T)/1 | 0/9 | 0/1 | 0/3 | AMBER | AMBER |  | It is felt the revised OPEX estimate should provide best endeavours to reduce risk of failing under an unannounced schedule, though no guarantee can be given. Process can suffer from dirty effluent decant. Improved storm/buffer tank may help to allow maximum treatment/retention time in CASS Basin. | Improved storm buffer tank and some tertiary treatment to catch any carryover. Sludge management of site possibly too small. Sludge storage and sludge thickening plant. | No
1 | Derrycrin | 1653.6 | 35300 | £8, 000 | 36953.6 | 8775.1 | 0 | 1582.5 | 10357.6 | 0/12 | 0/43 | 0/5 | 0/2 | 0/5 | RED (High) | GREEN |  | With the recently added package SAF along with the revised OPEX estimate should reduce risk of failing under an unannounced schedule, though no guarantee can be given. | SAF plant installed. No further Mature Compliance base maintenance required | Yes | 1
1 | Derrymore | 1622.4 | 0 | 36400 | 38022.4 | 6231.16 | 0 | 36400 | 42631.16 | 0/6 | 17/41 7/10/- | 0/8 | 0/1 | 0/1 | RED (High) | RED (HIGH) | Yes | Site suffers from flooding from L Neagh and process wash out, requiring regular re-seeding. Until addressed, OPEX will have limited impact on reducing compliance risk under an unannounced schedule. | Due to flood risk from Lough, base maintenance will have minimal impact on compliance. | No | 1
1 | Dundrum | 3244.8 | 0 | 2400 | 5644.8 | 17417.38 | 0 | 0 | 17417.38 | 3/22 (E.coli) | 1/44 0/1/- | 1/8 (8no E.coli exceedances) | 1/1 0/1/- | 0/2 | AMBER | RED (SEVERE) | Yes | The recent refurb of Dundrum was never design to meet the E.coli standard set. Unless a relaxation is obtained or disinfection treatment provided to meet standard, Dundrum will remain a projected failing. The recent upgrade seems to be meeting the remain parameters comfortably. | Possibility of E.coli standard being removed pending modelling. If removed Dundrum most likely would be a passing works, hydraulically and biologically. | Yes | 1
1 | Dunloy | 1622.4 | 0 | 0 | 1622.4 | 17309.23 | 1622.4 | 0 | 18931.63 | 0/12 | 4/43 0/1/3 | 0/6 | 0/1 | N/A | AMBER | AMBER |  | Revised OPEX estimate should provide best endeavours to reduce risk of failing under an unannounced schedule, though no guarantee can be given. Risk remains wth flow compliance. Although increased deep cleans should allow works to maintain current maximum levels that can be achieved, an upgrade with hi-flow MBR panels may be required. | Replacement of MBR panels with high flow membranes | Yes
1 | Edenderry | 1622.4 | 0 | 0 | 1622.4 | 7210.06 | 0 | 16000 | 23210.06 | 0/6 | 3/34 3/0/- | 0/4 | 0/1 | N/A | RED (High) | RED (HIGH) |  | Risk from age/condition of structural assets and flooding from River Lagan. Although the pilot shows a significant increase in OPEX it is felt realistically this will have minimal impact on reducing risk. Due to periods of low flows desludging activities would have a deterimental affect on the treatability. A capital intervention is felt the only viable option to address condition of assets, site flooding and compliance risk. | Due to flood risk from Lough, base maintenance will have minimal impact on compliance. | No | 1
1 | Galbally | 3244.8 | 0 | 0 | 3244.8 | 12001.47 | 0 | 1200 | 13201.47 | 1/6 | 6/42 2/4/- | 0/4 | 0/1 | N/A | RED (High) | RED (HIGH) |  | Risk is from the teritary treatment process which is ineffective and inefficient to operate and manage. Tertiary treatment is current by-passed with an interim arrangement in place which requires manual intervention. If the tertiary treatment plant is replaced with an effective and efficient process to operate and maintain, then the revised OPEX estimate should reduce risk of failing under an unannounced schedule and possibly could be reduced. | No additional Mature Compliance Base Maintenance required. Efficient tertiary filter identified in normal base maintenance discussions. | No | 1
1 | Jonesborough | 2433.6 | 0 | 2400 | 4833.6 | 5761.49 | 0 | 2400 | 8161.49 | 0/6 | 8/44 4/3/1 | 0/4 | 0/1 | N/A | AMBER | AMBER |  | Revised OPEX estimate should provide best endeavours to reduce risk of failing under an unannounced schedule, though no guarantee can be given. Risk remains wth flow compliance. Risk from 'spring slough', and infrequent unauthorised discharges. Tertiary treatment should remove carry over risk. There is sufficient room for a reed bed. | Provide tertiary treatment and increase final settlement capacity. | No
1 | Killygonlan | 3244.8 | 0 | 0 | 3244.8 | 9356.69 | 0 | 7200 | 16556.69 | 3/12 | 27/41 2/25/- | 5/6 | 0/1 | 1/15 1/0/0 | RED (High) | RED (SEVERE) | Yes | Process suffers from significant network infiltration, secondary treatment is overloaded and site prone to flooding. Until these issues are satisfactorily resolved will remain at significant risk. | No additional Mature Compliance Base Maintenance required | Yes | 1
1 | Kilrea | 4867.2 | 0 | 18400 | 23267.2 | 8730.73 | 0 | 16000 | 24730.73 | 0/12 | 2/35 2/0/- | 0/6 | 1/1 1/0/- | 0/1 | RED (High) | RED (HIGH) |  | Revised OPEX estimate should provide best endeavours to reduce risk of failing under an unannounced schedule, though no guarantee can be given. TE remains a concern which may have a bearing on future compliance | No additional Mature Compliance Base Maintenance required | Yes | 1
1 | Lisburn | 1622.4 | 0 | 0 | 1622.4 | 1352 | 0 | 0 | 1352 | 5/25 1/0/0 4no TP | N/A | 4/12 4no TP | 0/3 | N/A | AMBER | AMBER |  | With Lisburn being a manned site 7 days/week, the opportunity to increase OPEX to reduce risk of failing is limited, current OPEX should provide best endeavours to reduce risk of failing under an unannounced schedule, though no guarantee can be given. Flow compliance risk as process at times struggle to treat FFT. | No additional Mature Compliance Base Maintenance required | No | 1
1 | Liscolman | 4867.2 | 70400 | 18400 | 93667.2 | 5060.15 | 2500 | 16000 | 23560.15 | 0/6 | 11/38 0/0/11 | 0/2 | 0/2 | 1/1 1/0/0 | RED (High) | RED (HIGH) |  | The unannounced sample results indicate ammonia compliance remains a risk, which the sample month did not represent. The process would remain at significant risk requiring increased chemical dosing or capital intervention to provide effective treatment. May require further consideration. | Provision of side stream to operate when school is off. Periods of low flow. | No
1 | Lough Macrory | 2433.6 | 0 | 0 | 2433.6 | 7957.28 | 20800 | 0 | 28757.28 | 1/12 0/0/1 | 5/38 2/0/3 | 1/5 0/0/1 | 1/5 0/0/1 | 1/1 0/0/1 | AMBER | RED (HIGH) |  | Process is overloaded and struggles to treat to meet tight discharge consent. Revised OPEX estimate will not reduce this risk. Capital intervention required to upgrade process to meet current loading and discharge consent. Suffers from unauthorised discharges. | No additional Mature Compliance Base Maintenance required | Yes | 1
1 | Loughries | 1622.4 | 0 | 4800 | 6422.4 | 7210.06 | 0 | 16000 | 23210.06 | 5/9 3/0/2 | 32/28 13/9/10 | 14/8 7/3/4 | 0/1 | 24/18 16/8/0 | RED (High) | RED (SEVERE) | Yes | In its current stage the process will always struggle to achieve consent, any increase in OPEX will have minimal benefit. Site prone to flooding and structural assets in poor condition. Capital intervention to provide effective treatment and flooding required. | No additional Mature Compliance Base Maintenance required. Process is inadequate to meet the current WOC. | Yes | 1
1 | Maghera (DOWN) | 4056 | 0 | 2400 | 6456 | 5824.86 | 0 | 2400 | 8224.86 | 2/6 1/1/0 | 1/40 0/1/- | 0/5 | 0/1 | 0/1 | AMBER | AMBER |  | Revised OPEX estimate should provide best endeavours to reduce risk of failing under an unannounced schedule, though no guarantee can be given. Site suffers from flooding | No additional Mature Compliance Base Maintenance solution available | No | 1
1 | Meigh | 5896.8 | 0 | 2400 | 8296.8 | 5096.2 | 0 | 2400 | 7496.2 | 1/12 1/0/0 | 10/40 1/3/6 | 0/8 | 0/2 | 2/2 1/0/1 | RED (High) | RED (SEVERE) | Yes | Process is at capacity and struggles to treat to meet tight discharge consent. Revised OPEX estimate will not reduce this risk. Capital intervention required to upgrade process to meet current loading and discharge consent. Suffers from unauthorised discharges. Aeration recently upgraded under BM - improvement? | No additional Mature Compliance Base Maintenance solution available | Yes | 1
1 | Newcastle | 9734.4 | 0 | 0 | 9734.4 | 12848.02 | 0 | 0 | 12848.02 | 25 | 1/39 1/0/- | 0/13 | 0/1 | 0/1 | AMBER | AMBER |  | The revised OPEX estimate should reduce risk of failing under an unannounced schedule, though there are complimentary capital interventions required. Tertiary filter required to ensure most effective UV treatment. Review of sludge treatment facilities required and upgraded to ensure effective sludge removal and treatment and management of MLSS levels. | No additional Mature Compliance Base Maintenance solution available. PC21 capital delivery project will capture complaince needs. | Yes | 1
1 | Newry | 14601.6 | 0 | 0 | 14601.6 | 1310.92 | 10400 | 0 | 11710.92 | 0/48 | 20/36 9(6)/11(7)/- | 0/29 | 0/1 | 9/24 9/0/0 | AMBER | RED (SEVERE) |  | With Newry being a manned site 7 days/week, the opportunity to increase OPEX to reduce risk of failing is limited, current OPEX should provide best endeavours to reduce risk of failing under an unannounced schedule, though no guarantee can be given. Unauthorised discharge risk. | No additional Mature Compliance Base Maintenance solution available. PC21 capital delivery project will capture complaince needs. | Yes | 1
1 | Portaferry | 1622.4 | 0 | 0 | 1622.4 | 28470.55 | 0 | 0 | 28470.55 | 1/12 1no E.coli | 1/41 0/1/- | 1/7 1/0/- | 0/2 | 0/1 | AMBER | AMBER |  | The revised OPEX estimate should reduce risk of failing under an unannounced schedule, though there are complimentary capital interventions required. Replacement of tertiary filter to a more maintenance friendly plant to ensure most effective UV treatment. | Upgrade of tertiary treatment process. Already identified in normal base maintenance discussions. | No
1 | Saintfield | 1622.4 | 0 | 0 | 1622.4 | 9831.9 | 0 | 0 | 9831.9 | 0/12 | 1/44 0/0/1 | 0/8 | 0/2 | 0/2 | AMBER | AMBER |  | Revised OPEX estimate should provide best endeavours to reduce risk of failing under an unannounced schedule, though no guarantee can be given. | No additional Mature Compliance Base Maintenance required | No | 1
1 | Seahill | 4867.2 | 0 | 0 | 4867.2 | 10880.64 | 0 | 0 | 10880.64 | 0/12 | N/A | 0/9 | 0/4 | 0/5 | AMBER | AMBER |  | Revised OPEX estimate should provide best endeavours to reduce risk of failing under an unannounced schedule, though no guarantee can be given. Flow management still an issue in high flows. | No additional Mature Compliance Base Maintenance required | No | 1
1 | Stewartstown | 5616 | 0 | £20, 800 | 5616 | 8675.01 | 0 | 10396.53 | 19071.54 | 0/12 | 0/44 | 0/5 | 0/2 | 0/12 | RED (High) | RED (HIGH) |  | Revised OPEX estimate should provide best endeavours to reduce risk of failing under an unannounced schedule, though no guarantee can be given. | No additional Mature Compliance Base Maintenance solution available. PC21 capital delivery project will capture complaince needs. | Yes | 1
1 | Tamnaherin | 3244.8 | 0 | 5200 | 8444.8 | 8521.58 | 0 | 5200 | 13721.58 | 1/13 0/1/0 | 3/32 0/3/0 | 1/9 1/0/0 | 1/9 1/0/0 | 0/3 | AMBER | RED (HIGH) |  | Revised OPEX estimate should provide best endeavours to reduce risk of failing under an unannounced schedule, though no guarantee can be given. Risk due to volume/velocity of receiving flow due wet weather. It is believed storm separation opportunity is limited. Upgrade of inlet works to improve management of receiving flows ie balance tank, to reduce flow velocity. | Storm inlet flow management. Provision of tertiary ttreatment. | No
1 | Upper Ballinderry | 1622.4 | 0 | 0 | 1622.4 | 5555.16 | 0 | 0 | 5555.16 | 0/6 | N/A | 0/3 | 0/2 | N/A | AMBER | AMBER |  | Revised OPEX estimate should provide best endeavours to reduce risk of failing under an unannounced schedule, though no guarantee can be given. | No additional Mature Compliance Base Maintenance required | No | 1
1 | Whitehouse | 6489.6 | 0 | 5200 | 11689.6 | 17041.96 | 0 | 0 | 17041.96 | 2/25 2no U/T -1 BOD, 1 SS (1no TN exceedance) | N/A | 0/28 (2no TN exceedances) | 0/4 | 0/2 | AMBER | GREEN |  | Revised OPEX estimate should provide best endeavours to reduce risk of failing under an unannounced schedule, though no guarantee can be given. Increased OPEX primarily to cover compliance tasks required over week-end. | No additional Mature Compliance Base Maintenance solution required. PC21 capital delivery project ill capture compliance needs | Yes | 1
|  | 165267.04 | 109200 | 168800 | 443267.04 | 318369.25 | 38484.8 | 187629.53 | 544483.58
122.8%

## Revised RAG Status
| 2018-03-01 | 2020-11-01 | RAG Status Definition
Red (Severe) | 13 | 17 | WwTWs predicted to fail that will not pass until significant capital investment is complete.
Red (High) | 41 | 34 | WwTWs that carry a high risk of being non compliant for a variety of reasons; design (underloaded, overloaded), networks issues, TE, rogue discharges. Exceedences and/or Upper Tier failures experienced in last few years. If unannounced sampling is introduced it will make achieving compliance consistently more difficult.
Amber | 77 | 73 | WwTWs that have experienced exceedences in the last 2 yrs (but no upper tier failures). If unannounced sampling is introduced some works will require additional resource and/or tankering to ensure compliance due to uncertainty of sampling regime. Small scale capital investment identified in some cases.
Green | 101 | 111 | Fully compliant WwTWs i.e. no exceedences in the last 2 yrs. If unannounced sampling is introduced some works will require additional resource to ensure compliance due to uncertainty of sampling regime.
Totals | 232 | 235
3 new sites: | Castle Archdale
Stoneyford
The Loup

## Base Maintenance Impact
| Site | 2020 RAG Status | Mature Compliance Base Maintenance Inervention | Design PE | Actual PE (AIR 20) | PC21 | Impact on 2020 RAG Status | Revised OPEX Cost | Impact on Revised OPEX Cost | Comment
1 | Aghalee | Amber | Replacement of MBR panels with high flow membranes | 2000 | 1111 | No | Amber | 17161.88 | 17161.88 | Chemical and physical cleans still required. This intervention only allows the appropriate flow throughput to be treated.
2 | Aghanloo | Red (Severe) | Improved inlet flow control (FFT and storm) and base maintenance on filter bed. Old assets in poor condition and site is at it's maximum loading. | 550 | 786 | Yes | Red (Severe) | 20421.08 | 20421.08 | Wait on the Capital Delivery Project
3 | Annsborough | Red (High) | A combination of storm removal from the network and the provision of a more effective and efficient inlet works to manage flows and either primary settlement or balancing tank. | 6334 | 5991 | Yes | Red (High) | 12759.52 | 12759.52 | Wait on the Capital Delivery Project
4 | Ardglass | Red (High) | Sludge management of site possibly too small. Sludge storage and sludge thickening plant. No matter what base maintenance is carried out, unless TE is managed the site will always be at risk. | 7600 | 2895 | Yes | Red (High) | 24884.08 | 24884.08 | £16K in Business Plan for report on Traders. Profiled 2025.
5 | Armoy | Red (High) | Inlet flow control. Storm removal from the network. Provide Sludge storage facilities. Observation - old assets in poor condition | 745 | 818 | No | Amber | 12991.33 | 4991.33 | £8000 allocated in revised OPEX estimate. If Mature Compliance base maintenance delivered then additional sludge tankering no longer required.
6 | Castlederg | Amber | Improved storm buffer tank and some tertiary treatment to catch any carryover. Sludge management of site possibly too small. Sludge storage and sludge thickening plant. | 4750 | 3902 | No | Green | £10.516.86 | 8834.16 | Potential reduction in OPEX if Mature Compliance Base Maintenance delivered. Estimated at global 16% from the original and depending how effective this intervention is, further reduction is possible.
7 | Dunloy | Amber | Replacement of MBR panels with high flow membranes | 1630 | 1424 | No | Green | 18931.4 | 18931.4 | Chemical and physical cleans still required. This intervention only allows the appropriate flow throughput to be treated.
8 | Jonesborough | Amber | Provide tertiary treatment and increase final settlement capacity. | 1002 | 599 | No | Green | 8161.49 | £6, 855.58 | Mature Compiance base maintenance intervention would require less site visits, thereby reducing OPEX estimate.
9 | Liscolman | Red (High) | Provision of side stream to operate when school is off. Periods of low flow. | 400 | 266 | No | Amber | 23560.15 | 20000 | Mature compliance base maintenance intervention would require less chemicals in low flow periods, thereby reducing OPEX estimate by £2,500 potentially, plus a reduction in site visits.
10 | Portaferry | Amber | Upgrade of tertiary treatment process. Already identified in normal base maintenance discussions but not enough money to complete. | 5287 | 3802 | No | Green | 28470.55 | 23915.26 | Mature compliance base maintenance intervention would require less site visits for M&E at tertiary plant and UV plant, thereby reducing OPEX estimate. Global 16% applied.
11 | Tamnaherin | Red (High) | Storm inlet flow management. Provision of tertiary treatment. | 470 | 393 | No | Amber | 13721.58 | 11526.13 | Mature compliance base maintenance intervention would require less site visits thereby reducing OPEX estimate. Global 16% applied.
[8 empty] | 181063.06 | 163424.84
[9 empty] | 90.26% | Approximately 10% reduction in Revised OPEX estimate if Mature Compliance base maintenance interventions were applied