_____________________________________________

_____________________________________________

Northern Ireland

Gas Transmission System

PRESSURE REPORT

December 2006

Premier Transmission Ltd

Phoenix Natural Gas Ltd

BGÉ (UK) Ltd

CONTENTS

1	Introduction	1

2	GAS tRANSMISSION NETWORK	2

2.1	Existing system	2

2.2	Proposed developments	2

3	MODEL Details	4

3.1	Demand	4

3.2	Supply	5

3.3	Model Assumptions	5

4	results of network modelling	7

4.1	Scenarios	7

4.1.1	Peak day analysis	7

4.1.2	Sensitivity case analysis	8

4.1.2.1	Sensitivity 1 - Corrib commencing 2009/10	8

4.1.2.2	Sensitivity 2 – Increased MDQ @ Ballylumford with a new profile, Corrib commencing 2008/9	9

4.1.2.3	Sensitivity 3 – A new 400MW CCGT in the Belfast area	10

5	discussion and Conclusions	11

6	Appendices	14

6.1	Appendix A – Demand profiles	14

| Rev | Date | Status | PTL | PHX | BGE |
| --- | --- | --- | --- | --- | --- |
|  | 22 November 2006 | Initial draft for comment | x |  | x |
| 1 | 1 December 2006 | Second draft incorporating comments | x |  | x |
| 2 | 11 December 2006 | Third draft incorporating comments | x |  | x |
| 3 | 12 December 2006 | Final Copy Issued to Ofreg | x |  | x |
| 4 |  |  |  |  |  |

# Introduction

This report provides information on the predicted pressures in the gas supply system to Northern Ireland for the years 2006/07 to 2012/13 inclusive based on capacity figures provided by Shippers. These seven years are consistent with the time period used to produce the 2006 Gas Capacity Statement for the Republic of Ireland.

The 2005 Study included a “shoulder-day” scenario modelling firm non power generation demand at 75%.  This analysis clearly showed that the off-peak conditions were not critical and so the current study is for peak day conditions only.

The model used was one consisting of all of the pipelines which supply the whole of Ireland and was similar to those used to produce the 2006 Gas Capacity Statement for the Republic of Ireland but with the addition of the pipelines between Twynholm and Coolkeeragh including the South - North pipeline. The Northern Ireland demands have been updated to reflect the latest information supplied by the Northern Ireland PS gas suppliers provided under their licences. Modelling the entire network to produce reliable results is essential due to the integrated nature of the system once the South-North pipeline has been commissioned.

Indications are that the new supply from the Corrib field is now expected to be delivered in time for the 2008/09 winter. It was also considered prudent to examine the case where the delivery of gas is delayed by one year.

It should be noted that this study was carried out to identify the physical capacity of the SNIP system and therefore the contractual limit of 8.08mscmd was not applied to limit the flows into this system. The effect of this limit is discussed in the body of the report.

The SNIP/NWP model has been calibrated by independent consultants and this calibration showed good agreement with actual pressures recorded on the system.

# GAS tRANSMISSION NETWORK

## Existing system

The Irish Gas Transmission System

The BGÉ high pressure transmission network consists of approximately 2,000kms of pipe and conveys gas from two entry points (the “Inch” and “Moffat” entry points) to directly connected customers and distribution networks throughout Ireland, as well as to connected systems at exit points in Scotland (the Scotland-Northern Ireland Pipeline), and the Isle of Man. The Moffat entry point, located onshore in Scotland, connects the Irish natural gas system to that belonging to National Grid in the UK, and allows for the importation of UK gas to Ireland via two sub-sea interconnectors. The Inch entry point, located in Cork, connects the Kinsale and Seven Heads gas fields to the onshore network. The Irish system has three compressor stations, Beattock and Brighouse Bay in southwest Scotland, and Midleton in southeast Ireland near Cork.

The Northern Ireland Gas Transmission System

The Scotland to Northern Ireland 600mm pipeline (SNIP) connects to the BGÉ system at Twynholm and has a maximum operating pressure of 75 barg. The pipeline is 135 km long and runs towards the coast near Stranraer and crosses the Irish Sea to terminate at Ballylumford Power Station, Island Magee. SNIP is owned and operated by Premier Transmission Ltd.

The Phoenix Transmission Pipeline (PTP) comprises a further 35kms of 600mm pipeline with a maximum operating pressure of 75 Barg and runs from Ballylumford via Carrickfergus to Belfast.

From Carrickfergus 112km of 450mm pipeline have recently been constructed to supply the power station at Coolkeeragh, Londonderry. This pipeline, the North-West Pipeline (NWP), is owned and operated by BGE (UK) Ltd. As well as Coolkeeragh, several distribution networks are being developed in towns adjacent to the pipeline by Firmus Energy.

A new 450mm pipeline connecting the Interconnector System to the North-West Pipeline has been constructed and has just been commissioned in line with the planned timetable for this project. This pipeline, called the South-North Pipeline (SNP), is 156 km long and extends from the IC2 landfall at Gormanston, Co. Meath in the Republic of Ireland to Ballyalbanagh on the North - West Pipeline, approximately 12km west of the Carrickfergus AGI. This pipeline will facilitate supplies to towns and industries in the corridor from Newry to Belfast (also being developed by Firmus) and in the longer term will be able to support the SNIP pipeline in meeting increased demand levels in Northern Ireland. The SNP was developed by BGE (UK) Ltd and will be included in the NI postalised transmission system.

## Proposed developments

Construction of the 145kms Mayo – Galway pipeline finished in October 2006 and will link the Corrib gas field to the Irish market. This pipeline will connect a proposed onshore terminal in Bellanaboy Co. Mayo, into the Pipeline to the West at Cappagh South AGI in Co. Galway. The Corrib development is proposed to commence flowing gas in 2008/09 and this new source of supply will reduce the volume of gas to be delivered to Ireland from Moffat.   This has a considerable effect on the pressures on the onshore section of pipelines in Scotland.

The following diagram shows the major existing pipeline systems supplying Northern Ireland together with the approved developments to the system.

# MODEL Details

## Demand

The base case demands supplied by the SNIP system, the North - West Pipeline and the South - North Pipeline are tabulated in the following table. The actual flow rate will vary according to the calorific value of the gas delivered which is currently predicted to be of the order of 40 MJ/m3 at Beattock and the volumes given in the table below assume that value for the CV. The average value calculated from actual daily values taken over period from October 2005 to the present time is 40.01 MJ/m3.

| Year | 2005 NI Pressure Report Booked Capacities |  | 2006 NI Pressure Report Booked Capacities |  |
| --- | --- | --- | --- | --- |
|  | kWh/day | Mscmd | kWh/day | Mscmd |
| 2006/07 | 82,563,973 | 7.431 | 81,995,029 | 7.379 |
| 2007/08 | 86,847,785 | 7.816 | 82,710,317 | 7.444 |
| 2008/09 | 88,970,517 | 8.007 | 85,381,676 | 7.684 |
| 2009/10 | 90,970,931 | 8.187 | 87,309,594 | 7.858 |
| 2010/11 | - | - | 87,981,571 | 7.918 |
| 2011/12 | - | - | 90,622,264 | 8.156 |
| 2012/13 | - | - | 91,840,954 | 8.266 |

The comparison shows that the total forecast level of demand predicted this year is lower than that predicted last year.  The reason for this is that the rate of growth of demand in both the new towns (Firmus) and Belfast has been reduced.  The date when capacity will need to be booked on the interconnectors is therefore put back in this case.

For demands in the Republic of Ireland the values used are based on the central demand case used to produce the 2006 Gas Capacity Statement for the Republic of Ireland; the demands are based on information derived from a number of sources including shippers.

This statement is available from the CER website at http://www.cer.ie/CERDocs/cer06150.pdf.

## Supply

The peak day supplies into the system are tabulated below.  This includes figures for a scenario where Corrib is delayed by one year from 2008/09 to 2009/10.

| Year | Peak Day Supply Flows (mscmd) |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
|  | Inch | Corrib commencing 2008/9 |  | Corrib commencing 2009/10 |  |
|  |  | Moffat | Corrib | Moffat | Corrib |
| 2006/07 | 4.10 | 27.88 | 0 | 27.88 | 0 |
| 2007/08 | 3.49 | 28.96 | 0 | 28.96 | 0 |
| 2008/09 | 3.23 | 21.69 | 9.31 | 31.0 | 0 |
| 2009/10 | 3.02 | 22.63 | 9.31 | 22.63 | 9.31 |
| 2010/11 | 2.85 | 23.75 | 8.56 | 23.00 | 9.31 |
| 2011/12 | 2.78 | 26.64 | 6.68 | 24.76 | 8.56 |
| 2012/13 | 2.74 | 28.67 | 5.34 | 27.33 | 6.68 |

These clearly show that the amount of gas delivered to Ireland through Moffat increases until the Corrib field delivers gas to the ROI transmission system. These supply rates are based on the central supply scenario detailed in the 2006 Gas Capacity Statement for the Republic of Ireland. The flows exclude compressor fuel demands which are calculated by the simulation program. It is worth noting that if Corrib commences in 2009/10 the Moffat flow rate reaches the stated capacity of the station of 31mscmd with the assumed calorific value of 40MJ/m3. The flows from Inch include gas supplied from storage which was not assumed to be present when the 2005 pressure report was produced.

## Model Assumptions

The network analysis model has been built incorporating the following features:

- All scenarios have been studied by simulating the 24-hour demand cycle over a period of 3 days to obtain repeatable results over the day.

- All demands are modelled in energy terms. Volumetric flow is calculated by the network analysis program by applying relevant gas calorific value. The RoI demands are published in the 2006 Gas Capacity statement, the Northern Ireland demands have been updated with new information received from the PS gas suppliers since the production of that document.

- For Ballylumford power station the same diurnal profile was used as in 2005 for the case where the demand was at the 38.1 GWh/day level. However for the sensitivity analysis where the demand at this station was raised to 49.96 GWh/day a new profile, supplied by SONI, was used. This profile is flatter in shape than the original one and is shown in Appendix A.

- Full gas quality tracking is implemented to track changes in gas compositions throughout the network to allow computation of delivered gas calorific value.

- The SNIP system, North-West and South-North Pipelines are modelled to the same level of detail as the RoI system. Northern Ireland is entitled to offtake 8.08mscmd at Twynholm and the capacity of Twynholm AGI is understood to be 8.64mscmd. Gas in excess of these levels was allowed to flow through Twynholm provided all system pressures were maintained so that the full capability of the system to transport gas could be evaluated; however it is important to note that there is currently no contractual means to flow levels in excess of 8.08mscm/d through SNIP. Where pressures could not be maintained at the system extremities, additional flow above the level taken at Twynholm is forwarded via the Interconnectors to the South-North Pipeline.  The capacity of the SNIP System varies depending on a number of factors including the off-take profiles and the downstream pressure at Twynholm.

- Maximum discharge pressure from Twynholm into the SNIP system is 75 barg; the contractual minimum pressure upstream of Twynholm is 56 barg.  Pressure in SNIP system is controlled by the downstream pressure available at Twynholm as there is a obligation to supply at the prevailing pressure. The pressure at Twynholm in turn depends on the condition in the Onshore Scotland system. The suction pressure at Beattock has been assumed to be 45 barg for the purposes of this report.

- The design pressure of the South-North Pipeline is 85 barg via the appropriate facilities at Gormanston.

- For flows of greater than 26 mscmd through Moffat, the Beattock Station discharge pressure will be based on a report previously commissioned from PLE to determine Beattock compressor station handling capabilities with flows greater than the design flow.

- Pressure losses of 2 barg have been adopted for modelling purposes across Carrickfergus and Ballyalbanagh and 2.5 barg has been adopted at Twynholm.

# results of network modelling

## Scenarios

The analysis was carried out at the peak day demand level for the period 2006/07 to 2012/13 inclusive. Three sensitivity scenarios were included to test the robustness of the system to potential changes in the base assumptions that could occur over this period. These scenarios are as follows:-

Sensitivity 1: The base case scenario but with Corrib delayed by a further year to commence supply in 2009/10.

Sensitivity 2: An increased load and revised profile for Ballylumford with the MDQ increased to 49.96 GWh/day with an associated profile provided by SONI.

Sensitivity 3: A new 400MW CCGT in the Belfast area from 2009/10 onwards. The years analysed were 2009/10 & 2012/13.

### Peak day analysis

The Twynholm regulator was operated at a constant hourly flow rate over the day and the Carrickfergus regulator was allowed to flow freely.

In 2011/12 and 2012/13 the Twynholm flow exceeds the contractual maximum level but the analysis shows that this pipeline is physically capable of supplying this volume of gas under the conditions detailed below. Limiting flows to the contractual maximum level pressures will increase the pressures seen at Coolkeeragh above the levels listed in the tables.

The results are shown in the following tables.

| Year |  | Moffat Flow |  | Beattock Discharge Pressure | Twynholm |  |  |  | Brighouse Bay |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  |  |  | Upstream Pressure |  | Flow |  | Flow |  | Inlet Pressure |  |  |
|  |  | (mscmd) |  | (Barg) | (Barg) |  | (mscmd) |  | (mscmd) |  | (Barg) |  |  |
| Limits |  |  |  | 85 | 56 (Min) |  | 8.08 |  | 18.3 |  | 52 (Min) |  |  |
| 2006/7 |  | 27.88 |  | 85.0 | 72.6 |  | 7.38 |  | 19.90 |  | 69.6 |  |  |
| 2007/8 |  | 28.96 |  | 85.0 | 70.7 |  | 7.44 |  | 21.52 |  | 67.2 |  |  |
| 2008/9 |  | 21.69 |  | 85.0 | 77.4 |  | 7.68 |  | 14.01 |  | 75.5 |  |  |
| 2009/10 |  | 22.63 |  | 85.0 | 76.7 |  | 7.86 |  | 14.77 |  | 74.6 |  |  |
| 2010/11 |  | 23.75 |  | 85.0 | 75.8 |  | 7.92 |  | 15.83 |  | 73.6 |  |  |
| 2011/12 |  | 26.64 |  | 85.0 | 73.0 |  | 8.16 |  | 18.49 |  | 70.3 |  |  |
| 2012/13 |  | 28.67 |  | 85.0 | 70.8 |  | 8.27Error: Reference source not found |  | 20.40 |  | 67.6 |  |  |
| Year | Twynholm |  | Gormanston (South-North) |  |  |  |  | C’fergus |  | B’lumford |  | C’keeragh |  |
|  | Pressure |  | Pressure |  |  | Flow |  | Flow |  | Pressure |  | Pressure |  |
|  | (Max) |  | (Max) / (Min) |  |  |  |  |  |  | (Min) |  | (Min) |  |
|  | (Barg) |  | (Barg) |  |  | (mscmd) |  | (mscmd) |  | (Barg) |  | (Barg) |  |
| Limits | 75 (Max) |  | 30 (Min) |  |  |  |  |  |  | 27 (Min) |  | 27 (Min) |  |
| 2006/7 | 69.8 |  | 52.5 /43.9 |  |  | 0 |  | 1.82 |  | 48.9 |  | 42.9 |  |
| 2007/8 | 68.4 |  | 50.4 / 41.3 |  |  | 0 |  | 1.88 |  | 46.5 |  | 40.1 |  |
| 2008/9 | 74.9 |  | 57.5 / 48.6 |  |  | 0 |  | 2.08 |  | 53.7 |  | 47.6 |  |
| 2009/10 | 74.0 |  | 55.0 / 45.8 |  |  | 0 |  | 2.20 |  | 51.1 |  | 44.5 |  |
| 2010/11 | 73.3 |  | 53.9 / 44.6 |  |  | 0 |  | 2.24 |  | 50.0 |  | 43.2 |  |
| 2011/12 | 70.7 |  | 49.6 / 42.3 |  |  | 0 |  | 2.41 |  | 45.4 |  | 37.5 |  |
| 2012/13 | 68.4 |  | 45.3 / 34.9 |  |  | 0 |  | 2.47 |  | 41.0 |  | 32.1 |  |

These results indicate that in the base case all of the minimum pressures on the system can be satisfied. These results do not include the duplication of the onshore system in Scotland; if this were to be carried out pressures on the system would be higher than those shown above.

### Sensitivity case analysis

#### Sensitivity 1 - Corrib commencing 2009/10

The following tables summarise the critical results obtained for this case. It should be noted that the flow through Beattock reaches the stated maximum of 31mscmd.

| Year | Moffat Flow | Beattock Discharge Pressure | Twynholm |  | Brighouse Bay |  |
| --- | --- | --- | --- | --- | --- | --- |
|  |  |  | Upstream Pressure | Flow | Flow | Inlet Pressure |
|  | (mscmd) | (Barg) | (Barg) | (mscmd) | (mscmd) | (Barg) |
| Limits |  | 85 | 56 (Min) | 8.08 | 18.3 | 52 (Min) |
| 2008/9 | 31.00 | 85 | 68.1 | 7.68 | 23.32 | 64.0 |

| Year | Twynholm | Gormanston (South-North) |  | C’fergus | B’lumford | C’keeragh |
| --- | --- | --- | --- | --- | --- | --- |
|  | Pressure | Pressure | Flow | Flow | Pressure | Pressure |
|  | (Max) | (Max) / (Min) |  |  | (Min) | (Min) |
|  | (Barg) | (Barg) | (mscmd) | (mscmd) | (Barg) | (Barg) |
| Limits | 75 (Max) | 30 (Min) |  |  | 27 (Min) | 27 (Min) |
| 2008/09 | 65.7 | 44.9 / 35.2 | 0 | 2.08 | 40.8 | 33.1 |

Although the pressures are satisfactory the flow of 23.32mscmd at Brighouse Bay compressor station exceeds the stated capacity of 23 mscmd and is well in excess of the of the design capacity of 18.3 mscmd. Among the measures being considered to address this potential constraint are commercial incentives to reduce peak day demand in the RoI (including use of the interconnector inventory product), enhancement of the Beattock & Brighouse Bay Compressor stations and the performance testing of the existing Scottish infrastructure. Performance testing of the Interconnector System has commenced and work in this area will continue in 2007.  When this work is complete the capacity of this part of the system will be clearly defined. However it is considered that the system is sufficiently robust to deal with this delay in the delivery of Corrib taking such factors into account.

#### Sensitivity 2 – Increased MDQ @ Ballylumford with a new profile, Corrib commencing 2008/9

All years were re-run with Ballylumford at the higher demand of 49.96 GWh/day with the associated profile as provided by SONI. Modelled pressure at Coolkeeragh was breached in 2012/13 therefore an extra model was run for that year in order to attempt to alleviate the low pressures seen at Coolkeeragh. The flow through Twynholm in that case was limited to 8.64mscmd with the balance forwarded via the Interconnectors to NI.

| Year | Moffat Flow | Beattock Discharge Pressure | Twynholm |  | Brighouse Bay |  |
| --- | --- | --- | --- | --- | --- | --- |
|  |  |  | Upstream Pressure | Flow | Flow | Inlet Pressure |
|  | (mscmd) | (Barg) | (Barg) | (mscmd) | (mscmd) | (Barg) |
| Limits |  | 85 | 56 (Min) | 8.08 | 18.3 | 52 (Min) |
| 2006/7 | 28.35 | 85.0 | 71.5 | 8.45 | 19.90 | 68.4 |
| 2007/8 | 30.03 | 85.0 | 69.4 | 8.51 | 21.52 | 65.8 |
| 2008/9 | 22.76 | 85.0 | 76.5 | 8.75 | 14.01 | 74.6 |
| 2009/10 | 23.70 | 85.0 | 75.7 | 8.93 Error: Reference source not found | 14.77 | 73.7 |
| 2010/11 | 24.82 | 85.0 | 74.8 | 8.99 Error: Reference source not found | 15.83 | 72.6 |
| 2011/12 | 27.71 | 85.0 | 71.8 | 9.22 Error: Reference source not found | 18.49 | 69.0 |
| 2012/13 | 29.74 | 85.0 | 69.5 | 9.33 Error: Reference source not found | 20.40 | 67.2 |
| 2012/13_A 14 | 29.74 | 85.0 | 69.5 | 8.64 Error: Reference source not found | 21.09 | 66.0 |

| Year | Twynholm | Gormanston (South-North) |  | C’fergus | B’lumford | C’keeragh |
| --- | --- | --- | --- | --- | --- | --- |
|  | Pressure | Pressure | Flow | Flow | Pressure | Pressure |
|  | (Max) | (Max) / (Min) |  |  | (Min) | (Min) |
|  | (Barg) | (Barg) | (mscmd) | (mscmd) | (Barg) | (Barg) |
| Limits | 75 (Max) | 30 (Min) |  |  | 27 (Min) | 27 (Min) |
| 2006/7 | 67.9 | 46.1 / 39.1 | 0 | 1.83 | 44.3 | 37.0 |
| 2007/8 | 66.7 | 42.9 / 35.6 | 0 | 1.88 | 41.0 | 33.8 |
| 2008/9 | 73.9 | 51.6 / 44.3 | 0 | 2.09 | 49.7 | 43.1 |
| 2009/10 | 72.8 | 48.9 / 41.3 | 0 | 2.21 | 46.9 | 39.6 |
| 2010/11 | 72.1 | 47.5 / 39.6 | 0 | 2.25 | 45.4 | 37.8 |
| 2011/12 | 69.5 | 42.2 / 33.6 | 0 | 2.42 | 40.0 | 30.7 |
| 2012/13 | 67.0 | 36.8 / 27.7 | 0 | 2.49 | 34.6 | 23.5 |
| 2012/13_A 15 | 66.9 | 43.2 / 34.7 | 0.73 | 1.76 | 39.3 | 30.7 |

These results show that the minimum pressure at Coolkeeragh can be maintained until 2012/13. In this year the pressure can be restored to a satisfactory level by reducing the flow along the SNIP by supporting the system with gas supplied through the interconnectors and the South –North pipeline. With the contractual limit of 8.08 mscmd flowing through Twynholm the pressures seen will be higher than those shown in the above table.

The situation that occurs when Corrib was delayed to 2009/10 with the increased demand for Ballylumford Power Station creates a need to reinforce the supply system. The flow through Beattock exceeds 32 mscmd and the flow through Brighouse Bay compressor approaches 25 mscmd which is well in excess of the respective 31 mscmd and 23 mscmd capacity limits. Currently it is therefore not considered possible to supply this increased MDQ at Ballylumford in this case due to the high flow through Beattock compressor station; this position will be reviewed when the final results of the capacity studying Scotland are available.

#### Sensitivity 3 – A new 400MW CCGT in the Belfast area

The years analysed in this case were 2009/10 and 2012/13. The new CCGT was supplied from just upstream of the Carrickfergus AGI.

The tables overleaf summarises the results for this scenario. These show that provided it is acceptable to support the supply system in Northern Ireland via the South - North pipeline satisfactory pressures can be maintained at Coolkeeragh.

| Year | Moffat Flow | Beattock Discharge Pressure | Twynholm |  | Brighouse Bay |  |
| --- | --- | --- | --- | --- | --- | --- |
|  |  |  | Upstream Pressure | Flow | Flow | Inlet Pressure |
|  | (mscmd) | (Barg) | (Barg) | (mscmd) | (mscmd) | (Barg) |
| Limits |  | 85 | 56 (Min) | 8.08 | 18.3 | 52 (Min) |
| 2009/10 | 22.44 | 85 | 76.8 | 8.47 | 13.97 | 74.9 |
| 2012/13 | 28.48 | 85 | 71.2 | 8.47 | 20.01 | 68.1 |

| Year | Twynholm | Gormanston (South-North) |  | C’fergus | B’lumford | C’keeragh |
| --- | --- | --- | --- | --- | --- | --- |
|  | Pressure | Pressure | Flow | Flow | Pressure | Pressure |
|  | (Max) | (Max) / (Min) |  |  | (Min) | (Min) |
|  | (Barg) | (Barg) | (mscmd) | (mscmd) | (Barg) | (Barg) |
| Limits | 75 (Max) | 30 (Min) |  |  | 27 (Min) | 27 (Min) |
| 2009/10 | 68.7 | 46.7 / 37.3 | 1.08 | 1.13 | 40.6 | 32.7 |
| 2012/13 | 68.8 | 47.9 / 38.2 | 1.38 | 1.11 | 40.5 | 32.0 |

# discussion and Conclusions

The main result from this report is that the pressure service available in Northern Ireland is sufficient to meet the shipper’s requirements as analysed in the base case when Corrib is delivered in time for the 2008/09 winter. This conclusion applies even if the delivery of the Corrib field is delayed by one year to 2009/10 although it should be noted that the capacity of Brighouse Bay Compressor Station is breached in this case, Beattock Compressor Station also reaches its stated capacity. However it is considered that commercial and engineering solutions are available which will make the system sufficiently robust to deal with this delay.

If the peak flow rate at Ballylumford power station is increased from 38.01 GWh/day to 49.96 GWh/day satisfactory pressures can be maintained without any modification needed to the way the system operates except for the final year (2012/13). By limiting the flow through Twynholm satisfactory pressures can be met at Coolkeeragh; however this is at the expense of increasing the amount of gas that needs to be supplied via the South - North Pipeline to Northern Ireland.

If Corrib is delayed until 2009/10 with an increased MDQ at Ballylumford the flows through Beattock and Brighouse Bay are well in excess of the station capacity. Currently it is not thought that the engineering solutions available by that date are sufficient to meet this increased level of demand.  However the “flip-flop” arrangement in the PTL Transportation Code, does provide a commercial solution to address this scenario in Northern Ireland.

The case where a new gas fired power station was added to the system from 2009/10 onwards showed that the system could maintain satisfactory pressures. However in both of the years studied it was necessary to supply gas to Northern Ireland via the South - North pipeline.

All of the results in this report were obtained without applying any contractual limits to the flow through the SNIP system in order to determine the physical limits of the system. However if the 8.08mscmd limit is applied to the SNIP system, pressures on the system in Northern Ireland will improve in all cases as the system will receive additional support via the South – North pipeline.

- IMPORTANT NOTICE

Whilst every effort has been made to ensure the accuracy of the information contained in this report, neither Premier Transmission Limited, BGE & BGE (UK) Limited or Phoenix Natural Gas Limited  nor any of their respective employees, officers, directors, agents, advisers or other representatives make any representation, as to fact or law, express or implied in connection with this report.  No responsibility or liability is or will be accepted by any such persons in connection with the accuracy, completeness or sufficiency of this report (whether or not any error or mis-statement is negligent or otherwise) or the information contained in it.

# Appendices

## Appendix A – Demand profiles

There are two main demand profiles in use which show the variation in the hourly demand over the day. These profiles are for the Ballylumford Power Station and for the city of Belfast. These profiles are displayed graphically below and overleaf.

SONI provided one demand scenario which an associated profile that was utilised for the Sensitivity 2 analysis, the 2005 SONI profile was utilised in all other cases.

Coolkeeragh power station was assumed to be operating as a base load station to a flat profile (the hourly demand is 1/24th of the daily demand).

The Belfast demand profile has a distinct morning peak which reflects the fact that a larger proportion of the demand comes from the commercial and industrial market reflecting the way the load has built up in the city. As the domestic load increases this profile would be expected to move towards a more typical temperature sensitive diurnal with an evening peak. This profile is shown overleaf.

Inch flow excludes Midleton fuel gas and includes storage

Moffat flow excludes Beattock and Brighouse Bay fuel gas

Moffat flow equals its stated capacity of 31mscmd

Moffat flow excludes Beattock and Brighouse Bay fuel gas

Flow through Twynholm exceeds the contractual maximum of 8.08 Mscmd

The South-North pipeline is supplied from interconnector 2 via the AGI at Gormanston

The pressure at Ballylumford is that in the main pipeline

The Coolkeeragh pressure is upstream of the AGI

Moffat flow excludes Beattock and Brighouse Bay fuel gas

Brighouse Bay flow exceeds the stated capacity of 23mscmd

Moffat flow excludes Beattock and Brighouse Bay fuel gas

The present contractual maximum flow is 8.08 mscmd

Flow through Twynholm exceeds the station capacity of 8.64 mscmd

Moffat flow excludes Beattock and Brighouse Bay fuel gas

The present contractual maximum flow is 8.08 mscmd